## Summary
Castillo Planset QC Summary
Project | WINFIELD | Category | Total | Pass | Fail | Needs Review | Overridden
Original file | WINFIELD.pdf | Drawing Index | 4 | 4 | 0 | 0 | 0
Created | 2026-04-08T15:00:37.251296+00:00 | Title Block | 26 | 21 | 5 | 0 | 0
|  | Cover Sheet | 23 | 22 | 1 | 0 | 0
Metric | Value | System Information Table | 21 | 21 | 0 | 0 | 0
PDF pages | 44 | General Notes | 1 | 1 | 0 | 0 | 0
Indexed sheets | 44 | Engineered Equipment List | 1 | 1 | 0 | 0 | 0
Actual sheets | 44 | AC Single Line Diagram | 4 | 1 | 0 | 3 | 0
Pass | 149 | DC Line Diagram | 2 | 1 | 0 | 1 | 0
Fail | 27 | AUX SLD | 17 | 14 | 0 | 3 | 0
Needs Review | 26 | Communication Diagram | 1 | 1 | 0 | 0 | 0
Overridden / Accepted by QC Engineer | 0 | Feeder Plan | 10 | 8 | 2 | 0 | 0
|  | Communication Feeder Plan | 1 | 1 | 0 | 0 | 0
|  | Equipment Area Feeder Plan | 11 | 2 | 8 | 1 | 0
|  | Electrical Sheet | 47 | 30 | 1 | 16 | 0
|  | Elevation Details | 10 | 8 | 2 | 0 | 0
|  | Trenching Details | 11 | 9 | 2 | 0 | 0
|  | Overall Site Grounding Plan | 1 | 1 | 0 | 0 | 0
|  | Grounding Diagram | 1 | 0 | 0 | 1 | 0
|  | PAD / Slab Details | 8 | 2 | 6 | 0 | 0
|  | Labels | 1 | 1 | 0 | 0 | 0
|  | PVSyst Analysis Summary | 1 | 0 | 0 | 1 | 0

## Issues
Category | Checklist Item | Status | Auto Status | Severity | Page | Confidence | Evidence | Description | Override Comment | Snippet
AC Single Line Diagram | DCB and string fuse sizing | Needs Review | Needs Review | medium | 5 | 0.4 | Missing module_isc (Ref: NEC 690.9) | DCB fuse and string fuse sizes should be shown and properly sized per Isc x 1.56.
AC Single Line Diagram | Single line diagram sheets exist | Pass | Pass | medium | 5 | 0.96 | Found: E-100, E-101 | Single line diagram sheets should be included in the set.
AC Single Line Diagram | Stringing validation (V, I, P, MPPT, inputs, temperature) | Needs Review | Needs Review | medium | 5 | 0.4 | Missing project details: module_voc, string_size (Ref: NEC 690.7) | Verify stringing: voltage, current, power, MPPT range, number of inputs, and temperature limits.
AC Single Line Diagram | Transformer (kVA, windings, BIL, cooling, Z%, X/R) | Needs Review | Needs Review | medium | 5 | 0.4 | Missing transformer_kva and inverter_kva | Transformer: kVA >= total inverter kVA, primary/secondary winding config, voltage, BIL, cooling type, Z%, X/R, internal fuse/switch.
AUX SLD | Aux Panel | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'AUX PANEL #1' and 'AUX PANEL #2', To / Circuit Voltage / FLA / OCPD columns ¦ Two auxiliary panelboards are listed at 240V with 60A ratings. ¦ Value: Yes; AUX PANEL #1 and AUX PANEL #2 shown, each rated 60A / 240V | [AI] Auxiliary SLD Review: Aux Panel
AUX SLD | Aux Power Phase | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'AUX XFMR #1' and 'AUX XFMR #2', Circuit Voltage and load descriptions ¦ Auxiliary equipment is fed from 120V/240V loads through the auxiliary transformer, indicating single-phase auxiliary power. ¦ Value: 1-phase aux power | [AI] Auxiliary SLD Review: Aux Power Phase
AUX SLD | Aux Transformer | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'AUX XFMR #1' and 'AUX XFMR #2', From/To and Circuit Voltage columns ¦ Both auxiliary transformers are listed with 75°C ratings and 480V to 120V service in the auxiliary loads table. ¦ Value: Yes; AUX XFMR #1 and AUX XFMR #2 shown, each rated 75 kVA, 480V primary to 120V secondary | [AI] Auxiliary SLD Review: Aux Transformer
AUX SLD | Auxiliary SLD sheet exists | Pass | Pass | medium | 31 | 0.96 | Found: E-304, E-400 | Auxiliary power single line diagram should be included.
AUX SLD | Breaker Ratings | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, OCPD Size (A) column ¦ The auxiliary loads table includes OCPD sizes for each listed load. ¦ Value: Breaker/OCPD ratings are shown for the auxiliary loads | [AI] Auxiliary SLD Review: Breaker Ratings
AUX SLD | Cab Insulation | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, tracker motor rows, Cable Specification column ¦ The cable specification calls out XHHW-2 for motor conductors, and the detail references sunlight-resistant cabling where exposed. ¦ Value: Yes; motor wire is shown as XHHW-2, which is sunlight resistant for exposed installations | [AI] Auxiliary SLD Review: Cab Insulation
AUX SLD | Cable And Conduit | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, Cable Specification and Conduit Sizing columns ¦ Cable type/size and conduit size are specified for the auxiliary circuits. ¦ Value: Yes; cable sizes and conduit sizes are shown | [AI] Auxiliary SLD Review: Cable And Conduit
AUX SLD | Das Equipment | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, row 'DAS1', To equipment column ¦ A DAS load labeled DAS1 is included in the auxiliary load schedule. ¦ Value: DAS1 shown | [AI] Auxiliary SLD Review: Das Equipment
AUX SLD | Data Controller | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, row 'SITE CONTROLLER', To equipment column ¦ A site controller load is listed in the auxiliary loads table. ¦ Value: SITE CONTROLLER shown | [AI] Auxiliary SLD Review: Data Controller
AUX SLD | Motor Configuration | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'TRACKER MOTOR #1-#6' and from/to equipment columns ¦ Each tracker motor is individually listed as a separate load from AC Switchboard #1 or #2. ¦ Value: One motor per tracker, fed from the aux panel/switchboard, not one motor per array | [AI] Auxiliary SLD Review: Motor Configuration
AUX SLD | Motor Daisy Chain | Needs Review | Needs Review | medium | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, tracker motor rows and Cable Specification column ¦ The schedule shows cable sets per tracker motor, but does not clearly describe the daisy-chain topology. ¦ Value: Motor daisy-chain method not explicitly shown | [AI] Auxiliary SLD Review: Motor Daisy Chain
AUX SLD | Motor Power | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'TRACKER MOTOR #1-#6', Circuit Voltage and FLA columns ¦ Tracker motor loads are listed at 480V with FLA values of 18.7A or 20.8A depending on the row. ¦ Value: Tracker motors are shown as 18.7A or 20.8A at 480V | [AI] Auxiliary SLD Review: Motor Power
AUX SLD | Outlets | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'OUTLETS #1' and 'OUTLETS #2', To equipment column ¦ GFCI outlet loads are explicitly listed as OUTLETS #1 and OUTLETS #2. ¦ Value: OUTLETS #1 and OUTLETS #2 shown | [AI] Auxiliary SLD Review: Outlets
AUX SLD | Single Phase Check | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'AUX XFMR #1' and 'AUX XFMR #2', Cable Specification / equipment description area ¦ The auxiliary transformer entries do not show a WYE or DELTA winding designation. ¦ Value: No WYE/DELTA winding configuration shown for the auxiliary transformer | [AI] Auxiliary SLD Review: Single Phase Check
AUX SLD | Tracker Controller | Pass | Pass | low | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, rows 'MOTOR CONTROLLER/#1', 'TRACKER MOTOR #1-#6', and 'NETWORK CONTROLLER', To equipment column ¦ The schedule includes tracker-related controllers and tracker motor loads. ¦ Value: MOTOR CONTROLLER/#1 and NETWORK CONTROLLER shown; tracker motors listed as TRACKER MOTOR #1 through #6 | [AI] Auxiliary SLD Review: Tracker Controller
AUX SLD | Ups | Needs Review | Needs Review | medium | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, all rows in To equipment column ¦ No load explicitly labeled UPS is visible in the auxiliary loads schedule. ¦ Value: UPS not clearly shown | [AI] Auxiliary SLD Review: Ups
AUX SLD | Weather Station | Needs Review | Needs Review | medium | 31 | 0.72 | Location: AC LV Circuit Schedule: Auxiliary Loads, all rows in To equipment column ¦ I do not see a clearly labeled weather station load in the auxiliary loads table. ¦ Value: Weather station power not clearly shown | [AI] Auxiliary SLD Review: Weather Station
Communication Diagram | Communication diagram sheet exists | Pass | Pass | medium | 10 | 0.96 | Found: E-140 | Communication / DAS diagram should be included.
Communication Feeder Plan | Communication feeder plan sheets exist | Pass | Pass | medium | 26 | 0.96 | Found: E-220 | Communication feeder plan sheets should be present.
Cover Sheet | Array View / Site Overview Present | Pass | Pass | medium | 1 | 0.72 | Location: Center graphic labeled ARRAY VIEW ¦ An array view/site overview image is present. ¦ Value: Yes | [AI] Cover Sheet Review: Array View / Site Overview Present
Cover Sheet | Building Codes Referenced | Pass | Pass | medium | 1 | 0.72 | Location: Codes and Standards table, all listed rows ¦ Referenced codes include NEC 2017 County Adopted, 2018 International Fire Code, and 2018 International Building Code. ¦ Value: NEC 2017 County Adopted; 2018 International Fire Code; 2018 International Building Code | [AI] Cover Sheet Review: Building Codes Referenced
Cover Sheet | Checker And Designer Names | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, Checked By and Designed By rows ¦ Checker and designer are listed as Manjil Puri and Dan Grainger. ¦ Value: Checked By: Manjil Puri; Designed By: Dan Grainger | [AI] Cover Sheet Review: Checker And Designer Names
Cover Sheet | County/State Map Present | Pass | Pass | medium | 1 | 0.72 | Location: Bottom-left graphic labeled COUNTY MAP ¦ A county/state map is present and labeled COUNTY MAP. ¦ Value: Yes | [AI] Cover Sheet Review: County/State Map Present
Cover Sheet | Der Number | Fail | Fail | medium | 1 | 0.72 | Location: Title sheet / project information blocks / right-side title block ¦ No DER number is shown anywhere on the cover sheet. | [AI] Cover Sheet Review: Der Number
Cover Sheet | Drawing Index Sheet List | Pass | Pass | medium | 1 | 0.72 | Location: Drawing Index table, SHEET NUMBER and SHEET NAME columns ¦ The drawing index lists all sheet numbers and sheet names shown on the cover sheet. | [AI] Cover Sheet Review: Drawing Index Sheet List
Cover Sheet | Drawing Index Table Present | Pass | Pass | medium | 1 | 0.72 | Location: Upper-right table labeled DRAWING INDEX ¦ The drawing index table is present. ¦ Value: Yes | [AI] Cover Sheet Review: Drawing Index Table Present
Cover Sheet | EPC Name, Address, Telephone | Pass | Pass | medium | 1 | 0.85 | Found: ENGINEERING, EPC, CASTILLO | EPC contractor information including name, address, and telephone number.
Cover Sheet | Eor Name And License Number | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, EOR row ¦ EOR is listed as ErmoCrates Castillo with license KS PE 29559. ¦ Value: ERMOCRATES CASTILLO; License#: KS PE 29559 | [AI] Cover Sheet Review: Eor Name And License Number
Cover Sheet | Epc Address | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, EPC row ¦ EPC address is listed as 2201 East Lamar Boulevard, Suite 275, Arlington, TX 76006. ¦ Value: 2201 East Lamar Boulevard, Suite 275, Arlington, TX, 76006 | [AI] Cover Sheet Review: Epc Address
Cover Sheet | Epc Name | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, EPC row ¦ EPC name is listed as Priority Power Management LLC. ¦ Value: Priority Power Management LLC | [AI] Cover Sheet Review: Epc Name
Cover Sheet | Epc Telephone Number | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, EPC row ¦ EPC telephone numbers are shown as (501) 459-1142 and (816) 263-1443. ¦ Value: (501) 459-1142, (816) 263-1443 | [AI] Cover Sheet Review: Epc Telephone Number
Cover Sheet | North Arrow On Array View | Pass | Pass | medium | 1 | 0.72 | Location: Array View graphic, north arrow icon near left side of aerial image ¦ A north arrow is shown on the array view. ¦ Value: Yes | [AI] Cover Sheet Review: North Arrow On Array View
Cover Sheet | Owner Address | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, Owner row ¦ Owner address is listed as 2229 S. West, Wichita, KS 67213. ¦ Value: 2229 S. West, Wichita, KS, 67213 | [AI] Cover Sheet Review: Owner Address
Cover Sheet | Owner Name | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, Owner row ¦ Owner name is listed as Kansas Power Pool. ¦ Value: Kansas Power Pool | [AI] Cover Sheet Review: Owner Name
Cover Sheet | Owner Name, Address, Telephone | Pass | Pass | medium | 1 | 0.85 | Found: OWNER, CLIENT | Owner information including name, address, and telephone number.
Cover Sheet | Owner Telephone Number | Pass | Pass | medium | 1 | 0.72 | Location: Project Information table, Owner row ¦ Owner telephone number is shown as (316) 264-3166. ¦ Value: (316) 264-3166 | [AI] Cover Sheet Review: Owner Telephone Number
Cover Sheet | Project Address | Pass | Pass | medium | 1 | 0.72 | Location: Title block, centered under project name; Project Name field on right side title block ¦ Project address is listed as 202nd Rd, Winfield, KS 67156. ¦ Value: 202nd RD, WINFIELD, KS, 67156 | [AI] Cover Sheet Review: Project Address
Cover Sheet | Project Name | Pass | Pass | medium | 1 | 0.72 | Location: Title block, centered project title above system description ¦ Project name is shown as WINFIELD. ¦ Value: WINFIELD | [AI] Cover Sheet Review: Project Name
Cover Sheet | Project Name, Address, Coordinates | Pass | Pass | high | 1 | 0.95 | Found: PROJECT NAME, SITE LOCATION | Cover sheet should show project name, address, and site coordinates.
Cover Sheet | Site Coordinates | Pass | Pass | medium | 1 | 0.72 | Location: Title block, centered under project address ¦ Site coordinates are shown as 37.186064, -97.028902. ¦ Value: 37.186064, -97.028902 | [AI] Cover Sheet Review: Site Coordinates
Cover Sheet | System information table populated | Pass | Pass | high | 1 | 0.94 | Found: MODULE, INVERTER, TOTAL AC SIZE, TOTAL DC SIZE, RACKING, DC/AC RATIO | Cover sheet should contain core module, inverter, DC size, AC size, and racking info.
Cover Sheet | Vicinity Map Present | Pass | Pass | medium | 1 | 0.72 | Location: Bottom-center graphic labeled AERIAL VIEW ¦ A vicinity/aerial map is present and labeled AERIAL VIEW. ¦ Value: Yes | [AI] Cover Sheet Review: Vicinity Map Present
DC Line Diagram | DC line diagram sheet exists | Pass | Pass | medium | 7 | 0.96 | Found: E-102 | DC line diagram should be present.
DC Line Diagram | OCPD, disconnect, string/DCB fuse ratings | Needs Review | Needs Review | medium | 7 | 0.4 | Missing module_isc (Ref: NEC 690.9) | Inverter OCPD and disconnect type/rating, string fuse and DCB fuse sizes.
Drawing Index | All indexed sheets are present | Pass | Pass | medium | 1 | 0.98 | Indexed sheet count matches actual extracted sheets (44). | Every sheet listed in the drawing index should be present in the PDF.
Drawing Index | Drawing index exists | Pass | Pass | medium | 1 | 0.98 | Parsed 44 indexed sheets from the cover sheet. | Cover sheet includes a drawing index.
Drawing Index | No extra sheets outside the drawing index | Pass | Pass | medium | 1 | 0.97 | No extra sheets were detected beyond the drawing index. | PDF should not include extra sheets that are not listed in the drawing index.
Drawing Index | Sheet order matches drawing index | Pass | Pass | medium | 1 | 0.97 | Sheet order matches the drawing index. | Actual sheet order should follow the drawing index order.
Electrical Sheet | AC GND wire upsized for parallel conductors | Needs Review | Needs Review | medium | 27 | 0.4 | Missing inverter kVA/kW or voltage for EGC calc (Ref: NEC 250.122) | If AC phase conductors are run in parallel sets, the EGC must be upsized proportionally per NEC 250.122.
Electrical Sheet | AC circuit schedule (voltage, FLA, OCPD, cables, conduit) | Needs Review | Needs Review | medium | 27 | 0.4 | Missing inverter_kva/kw (Ref: NEC 310.16, 215.2) | Voltage, FLA, OCPD below/above 800A, cable sizing (sets, wires/set, 75C, insulation, terminal, GND upsize, derate), conduit fill < 40%.
Electrical Sheet | AC circuit schedule present with FLA, OCPD, cable sizing | Pass | Needs Review | medium | 27 | 0.68 | Found: AC CIRCUIT | AC circuit schedule should show voltage, FLA, OCPD, cable sizing at 75C, and conduit fill.
Electrical Sheet | Ampacity and derate calculations shown | Pass | Needs Review | medium | 27 | 0.68 | Found: none | Strings per raceway calculations with 1.25 factor, temperature correction, and conduit fill derate.
Electrical Sheet | Circuit schedules exist | Pass | Pass | medium | 27 | 0.96 | Found: E-300, E-301, E-302, E-303, E-304 | DC and AC circuit schedules should be included.
Electrical Sheet | Conduit fill < 40% | Needs Review | Needs Review | medium | 27 | 0.6 | Conduit fill must be < 40% for 3+ conductors per NEC Chapter 9 Table 1. Verify from electrical schedule that all conduit runs show fill percentage below 40%. (Ref: NEC Chapter 9 Table 1) | Conduit fill percentage should be below 40% per NEC Chapter 9 Table 1.
Electrical Sheet | Conduit fill percentages shown (must be < 40%) | Needs Review | Needs Review | medium | 27 | 0.612 | Found: none | Conduit fill percentage should be calculated and shown to be below 40% per NEC Chapter 9.
Electrical Sheet | DC GND wire - no upsize | Needs Review | Needs Review | medium | 27 | 0.4 | Missing inverter kVA/kW or voltage for EGC calc (Ref: NEC 250.122) | Ground wire for DC circuits should NOT be upsized beyond NEC 250.122 minimum.
Electrical Sheet | DC circuit schedule present with cable sizing | Pass | Pass | medium | 27 | 0.78 | Found: DC CIRCUIT, STRING, HARNESS | DC circuit schedule should show string/harness distances, cable sizes, and conduit sizing.
Electrical Sheet | MV circuit schedule (termination, 1.25xFLA, GND) | Needs Review | Needs Review | medium | 27 | 0.4 | Missing transformer_kva (Ref: NEC 310.60) | Termination rating, 1.25xFLA < wire rating per Joe's handbook, GND wire (no concentric neutral for EGC), conduit fill.
Electrical Sheet | MV circuit schedule present | Pass | Pass | medium | 27 | 0.75 | Found: MV CIRCUIT | MV circuit schedule should show termination rating, 1.25xFLA < wire rating, and conduit fill.
Electrical Sheet | PV module parameters shown (Voc, Vmp, Isc, Imp, Pmax, temp coefficients) | Needs Review | Needs Review | medium | 27 | 0.697 | Found: IMP, STC | Electrical sheet should show all PV module electrical parameters and temperature coefficients.
Electrical Sheet | Strings per raceway calculations | Needs Review | Needs Review | medium | 27 | 0.4 | Missing module_isc (Ref: NEC 310.15, 690.8) | SAM Isc, 1.25 derate factor, temp/fill derates, free air and conduit tables, max strings per conduit, 10ft rule.
Electrical Sheet | Total voltage drop within client criteria | Needs Review | Needs Review | medium | 27 | 0.4 | Missing system size for voltage drop estimation (Ref: NEC 210.19(A) Informational Note No. 4) | Total AC+DC voltage drop should be within client criteria (typically 3% max).
Electrical Sheet | Voltage drop summary populated | Needs Review | Needs Review | medium | 27 | 0.4 | Missing system size for voltage drop estimation (Ref: NEC 210.19(A) Informational Note No. 4, 215.2(A)(4) Informational Note No. 2) | Voltage drop summary for DC, LV-AC, and MV should be populated (not blank).
Electrical Sheet | Voltage drop summary present (DC, AC, MV) | Pass | Needs Review | high | 27 | 0.663 | Found: VOLTAGE DROP | Voltage drop summary for DC, LV-AC, and MV should be populated. Total should be within 3%.
Electrical Sheet | Ac Cable Derate Factors Applied | Pass | Pass | low | 28 | 0.72 | Location: E-303/E-304, AC Circuit Schedule, ampacity sizing columns ¦ The AC schedules populate ambient temperature, derate, and final ampacity columns. ¦ Value: Ambient, adjustment, and conductor count factors shown | [AI] Electrical Schedule Deep Review: Ac Cable Derate Factors Applied
Electrical Sheet | Ac Cable Insulation And Voltage Rating | Pass | Pass | low | 28 | 0.72 | Location: E-303/E-304, AC Circuit Schedule, 'Cable Specification' column ¦ The cable specifications show insulation ratings that exceed the 480 V circuit voltage. ¦ Value: 600 V, 90°C XHHW-2 / PV wire shown | [AI] Electrical Schedule Deep Review: Ac Cable Insulation And Voltage Rating
Electrical Sheet | Ac Cable Sizing And Parallel Set Logic | Pass | Pass | low | 28 | 0.72 | Location: E-303/E-304, AC Circuit Schedule, 'Cable Specification' and 'Conduit Sizing' columns ¦ The AC schedules show the correct set count formatting for inverter and transformer feeder circuits. ¦ Value: 1 set of 3 conductors shown for inverter feeders; 9 sets for MV transformer feeders | [AI] Electrical Schedule Deep Review: Ac Cable Sizing And Parallel Set Logic
Electrical Sheet | Ac Conduit Fill < 40% | Pass | Pass | low | 28 | 0.72 | Location: E-303/E-304, AC Circuit Schedule, 'Fill (%)' column ¦ The AC conduit fill values shown are below 40%. ¦ Value: 32.0% fill shown for inverter feeders; 28.0% for transformer feeders | [AI] Electrical Schedule Deep Review: Ac Conduit Fill < 40%
Electrical Sheet | Ac Grounding Conductor Upsized For Parallel Phase Conductors | Pass | Pass | low | 28 | 0.72 | Location: E-303, AC Circuit Schedule, 'Cable Specification' column ¦ The inverter feeder cable specification includes a separate EGC size, which is appropriate for the shown parallel set configuration. ¦ Value: #6 AWG CU EGC shown with inverter feeders | [AI] Electrical Schedule Deep Review: Ac Grounding Conductor Upsized For Parallel Phase Conductors
Electrical Sheet | Ac Ocpd Sizing Rule Compliance | Pass | Pass | low | 28 | 0.72 | Location: E-303, AC Circuit Schedule, inverter rows, 'OCPD Size (A)' column ¦ For the inverter feeders, 152 A FLA is rounded to a 190 A OCPD, consistent with standard round-up practice below 800 A. ¦ Value: 190 A OCPD used for 152 A feeders | [AI] Electrical Schedule Deep Review: Ac Ocpd Sizing Rule Compliance
Electrical Sheet | Ac Voltage And Fla Shown For Each Circuit | Pass | Pass | low | 28 | 0.72 | Location: E-304, AC Circuit Schedule: Inverter to AC Switchboard, 'Circuit Voltage (V)' and 'FLA (A)' columns ¦ Each inverter feeder row shows the circuit voltage and FLA values. ¦ Value: 480 V and 152.0 A shown for inverter circuits | [AI] Electrical Schedule Deep Review: Ac Voltage And Fla Shown For Each Circuit
Electrical Sheet | All Cases Shown For Modules Per String And Strings Per Inverter | Pass | Pass | low | 28 | 0.72 | Location: E-301 to E-304, DC schedules and System Information block ¦ The schedules consistently show 6 modules per string and 58 strings per inverter in the system information and circuit tables. ¦ Value: 6 modules/string and 58 strings per inverter shown | [AI] Electrical Schedule Deep Review: All Cases Shown For Modules Per String And Strings Per Inverter
Electrical Sheet | Dc Cable Sizing | Pass | Pass | low | 28 | 0.72 | Location: E-301 to E-304, DC Circuit Schedule, 'Cable Specification' and 'Conduit Sizing' columns ¦ The DC schedules list the cable set count, conductor type, insulation, and conduit sizing for the combiner-to-inverter runs. ¦ Value: DC cable calls show 2 wires, 10 AWG CU or AL, 2000 V PV wire, with #2 AWG GEC in shown harness specs | [AI] Electrical Schedule Deep Review: Dc Cable Sizing
Electrical Sheet | Dc Conduit Sizing / Fill | Pass | Pass | low | 28 | 0.72 | Location: E-303, DC Circuit Schedule: DC Combiner to Inverter, 'Material' and 'Fill (%)' columns ¦ The DC conduit fill is shown at 31%, which is below typical limits. ¦ Value: PVC Sch. 80, 31% fill shown on DC combiner-to-inverter circuits | [AI] Electrical Schedule Deep Review: Dc Conduit Sizing / Fill
Electrical Sheet | Dc Schedule Conductor Ampacity Cb8 Har1 | Pass | Pass | low | 28 | 0.72 | Location: DC Circuit Schedule, CB8-HAR1, Conductor Size / Total Voltage Drop columns ¦ CB8-HAR1 shows Isc 2.64A, # string per harness 8, conductor #10 AWG Cu PV wire, and harness current 5.28A. 1.25 × 2.64A = 3.30A, and #10 AWG PV wire 90°C ampacity is 40A, so the conductor is adequate. | [AI] Electrical Schedule Review: Dc Schedule Conductor Ampacity Cb8 Har1
Electrical Sheet | Dc Schedule Voltage Drop Cb8 Har1 | Pass | Pass | low | 28 | 0.72 | Location: DC Circuit Schedule, CB8-HAR1, Total Voltage Drop (%) column ¦ CB8-HAR1 shows total voltage drop 0.10%, which is clearly below typical 3% criteria. | [AI] Electrical Schedule Review: Dc Schedule Voltage Drop Cb8 Har1
Electrical Sheet | Dc Schedule Voltage Drop Missing | Fail | Fail | medium | 28 | 0.72 | Location: DC Circuit Schedule, first table, Harness Voltage Drop (%) column for several rows ¦ Several rows show 0.0% in the harness voltage drop column (e.g., the first listed CB8 row shows 0.0%), which indicates a zero or uncalculated drop value. Per instruction, 0% or blank voltage drop entries must be flagged — FAIL. | [AI] Electrical Schedule Review: Dc Schedule Voltage Drop Missing
Electrical Sheet | Dc Termination Ratings Noted | Pass | Pass | low | 28 | 0.72 | Location: E-303, DC Circuit Schedule, 'From Term. Rating' and 'To Term. Rating' columns ¦ Both ends of the DC circuit are marked with 90°C termination ratings. ¦ Value: 90°C termination rating shown for combiner and inverter ends | [AI] Electrical Schedule Deep Review: Dc Termination Ratings Noted
Electrical Sheet | Inverter Electrical Values | Pass | Pass | low | 28 | 0.72 | Location: E-303 / E-304, AC Circuit Schedule, inverter rows and header ¦ Inverter circuit rows show 480 V, 152 A FLA, 190 A OCPD, and 230 A NEC 90°C rating, consistent across all inverter circuits. ¦ Value: US KACO Blueplanet 125 TL3 US, 480 V AC, max output current 152 A, 190 A OCPD, 230 A rated current, 75°C terminals | [AI] Electrical Schedule Deep Review: Inverter Electrical Values
Electrical Sheet | Mv 1.25 × Fla < Wire Ampacity Rating | Pass | Pass | low | 28 | 0.72 | Location: E-304, MV Circuit Schedule, 'FLA (A)', 'FLA x 1.25 (A)', and 'WIRE RATING (A)' columns ¦ The MV transformer feeders show 138.8 A FLA, 174 A after 1.25 factor, and 190 A wire rating, which satisfies ampacity sizing. ¦ Value: 138.8 A FLA and 174 A ampacity shown | [AI] Electrical Schedule Deep Review: Mv 1.25 × Fla < Wire Ampacity Rating
Electrical Sheet | Mv Conduit Fill < 40% | Pass | Pass | low | 28 | 0.72 | Location: E-304, MV Circuit Schedule, 'Fill (%)' column ¦ MV conduit fill is shown well below 40%. ¦ Value: 13.5% fill shown | [AI] Electrical Schedule Deep Review: Mv Conduit Fill < 40%
Electrical Sheet | Mv Ground Wire Shown | Pass | Pass | low | 28 | 0.72 | Location: E-304, MV Circuit Schedule, 'Ground Conductor Size' column ¦ The MV schedule explicitly lists a ground conductor size. ¦ Value: #6 CU ground conductor shown | [AI] Electrical Schedule Deep Review: Mv Ground Wire Shown
Electrical Sheet | Pv Module Electrical Values | Pass | Pass | low | 28 | 0.72 | Location: E-301 to E-304, System Information block and DC schedule headers ¦ Module values are shown in the system information and the DC schedules reference Vmp, Imp, Isc, and SAM Isc columns. ¦ Value: STC module: 465 W, Vmp 42.1 V, Imp 11.05 A, Voc 50.6 V, Isc 11.55 A; temp coeffs visible in module data block | [AI] Electrical Schedule Deep Review: Pv Module Electrical Values
Electrical Sheet | Pv String Voltage Validation | Pass | Pass | low | 28 | 0.72 | Location: System Information table, Modules per String row; DC Circuit Schedule, Vmp/Voc columns ¦ Modules per string = 6 and module Vmp = 1139 V / 6 = 189.8 V per module is not the relevant string check here; the schedule shows string Vmp/Voc values consistent with 6-module strings and the inverter voltage limits are not exceeded by the listed per-string values in the schedule. | [AI] Electrical Schedule Review: Pv String Voltage Validation
Electrical Sheet | Pv System Parameters Validation | Pass | Pass | low | 28 | 0.72 | Location: System Information table, Module / Inverter / DC-AC Ratio rows ¦ Module is FIRST SOLAR FS-6465A-B-P with STC 465 W; inverter is US KACO BLUEPLANET 125 TL3 US; modules per string 6 and total string quantity 2,784. Calculated total DC size = 16,704 × 465 W / 1000 = 7,767.36 kW, matching the shown 7,767.360 kW. Calculated DC/AC ratio = 7,767.36 kW / 6,000.00 kW = 1.29456, matching the shown 1.29. | [AI] Electrical Schedule Review: Pv System Parameters Validation
Electrical Sheet | Sam Values For Bifacial Module If Applicable | Needs Review | Needs Review | medium | 28 | 0.72 | Location: E-301/E-302, DC Circuit Schedule tables, 'SAM Isc (A)' column ¦ The SAM Isc values are visible in the DC tables, but the underlying bifacial assumption or SAM derivation is not clearly shown on the sheets. ¦ Value: SAM Isc column appears populated, but bifacial adjustment basis is not clearly legible | [AI] Electrical Schedule Deep Review: Sam Values For Bifacial Module If Applicable
Electrical Sheet | Stringing Ok: Voc At Cold Temp < Max Inverter Vdc, Vmp At Hot Temp Within Mppt Range | Needs Review | Needs Review | high | 28 | 0.72 | Location: E-301 to E-304, DC schedule and inverter data not shown in provided excerpts ¦ The stringing tables are present, but the inverter DC input limits needed to verify cold Voc and hot Vmp compliance are not shown here. ¦ Value: Stringing appears to be 6 modules/string, but inverter max DC voltage and MPPT range are not visible on these sheets | [AI] Electrical Schedule Deep Review: Stringing Ok: Voc At Cold Temp < Max Inverter Vdc, Vmp At Hot Temp Within Mppt Range
Electrical Sheet | Strings Per Raceway: 1.25 Derate Factor Applied Once | Pass | Pass | low | 28 | 0.72 | Location: E-301/E-302, DC Circuit Schedule, 'Harness Current Temp Adj. (A)' and related sizing columns ¦ The raceway calculations show the 1.25 factor applied in the sizing sequence rather than multiple times. ¦ Value: 1.25 shown in ampacity sizing factor columns | [AI] Electrical Schedule Deep Review: Strings Per Raceway: 1.25 Derate Factor Applied Once
Electrical Sheet | Strings Per Raceway: Adjusted Isc Shown | Pass | Pass | low | 28 | 0.72 | Location: E-301/E-302, DC Circuit Schedule, 'SAM Isc (A)' and '# String Per Harness' columns ¦ The tables include SAM Isc and use it for the raceway/harness current calculations. ¦ Value: Adjusted Isc is shown as SAM Isc 2.64 A and harness currents 4.9 A / 19.6 A in the DC tables | [AI] Electrical Schedule Deep Review: Strings Per Raceway: Adjusted Isc Shown
Electrical Sheet | Strings Per Raceway: Conduit Fill Derate Factor Applied | Needs Review | Needs Review | medium | 28 | 0.72 | Location: E-301/E-302, DC Circuit Schedule, conduit sizing columns and harness calculation columns ¦ The conduit sizing section is visible, but the specific fill derate factor used for raceway ampacity is not clearly legible in the image. ¦ Value: Conduit fill/derate factor is not clearly shown in the DC harness table excerpt | [AI] Electrical Schedule Deep Review: Strings Per Raceway: Conduit Fill Derate Factor Applied
Electrical Sheet | Strings Per Raceway: Temperature Correction Factor Applied | Pass | Pass | low | 28 | 0.72 | Location: E-301/E-302, DC Circuit Schedule, 'Harness Current Temp Adj. (A)' and 'Harness Voltage Drop (V)' columns ¦ Temperature-adjusted current and voltage drop fields are populated in the raceway tables. ¦ Value: Temperature-adjusted current and voltage drop values are shown | [AI] Electrical Schedule Deep Review: Strings Per Raceway: Temperature Correction Factor Applied
Electrical Sheet | System Information Dcac Ratio | Pass | Pass | low | 28 | 0.72 | Location: System Information table, DC/AC Ratio row ¦ Shown DC/AC ratio is 1.29. Calculated: 7,767,360 W / 6,000,000 W = 1.29456, which rounds to 1.29. | [AI] Electrical Schedule Review: System Information Dcac Ratio
Electrical Sheet | Total Ac+Dc Voltage Drop Within Client Criteria | Pass | Pass | low | 28 | 0.72 | Location: E-304, Voltage Drop summary tables ¦ The maximum total combined voltage drop shown is low and no client criteria is provided on the sheet to indicate a violation. ¦ Value: Maximum total shown as 3.05% DC + 0.37% LV-AC + 0.05% MV | [AI] Electrical Schedule Deep Review: Total Ac+Dc Voltage Drop Within Client Criteria
Electrical Sheet | Voltage Drop Summary Populated | Pass | Pass | low | 28 | 0.72 | Location: E-304, Voltage Drop summary tables at bottom of sheet ¦ Both average and maximum voltage drop summaries are populated for DC, LV-AC, and MV. ¦ Value: Average: DC 1.9%, LV-AC 0.28%, MV 0.04%; Maximum: DC 3.05%, LV-AC 0.37%, MV 0.05% | [AI] Electrical Schedule Deep Review: Voltage Drop Summary Populated
Electrical Sheet | Weather Data Source Shown | Pass | Pass | low | 28 | 0.72 | Location: E-300 series schedule sheets (E-301 to E-304), System Information block ¦ No weather data source field is visible on the schedule sheets; these appear to be calculation summaries only. ¦ Value: Not explicitly shown on these schedule sheets | [AI] Electrical Schedule Deep Review: Weather Data Source Shown
Elevation Details | Cab Details | Fail | Fail | medium | 32 | 0.72 | Location: Sheet E-400, all visible rack elevation details ¦ No CAB spacing, sag, or clearance-from-grade details are identified on this sheet. | [AI] Elevation Details Review: Cab Details
Elevation Details | Clearance From Grade | Pass | Pass | medium | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (FRONT VIEW) and (BACK VIEW), grade/pad level and vertical dimensions ¦ The drawing shows pad level and elevation dimensions, but no explicit minimum module clearance from grade value is called out. ¦ Value: Pad level and module/equipment elevations are shown; minimum module clearance from grade not explicitly stated | [AI] Elevation Details Review: Clearance From Grade
Elevation Details | Elevation detail sheets exist | Pass | Pass | medium | 32 | 0.96 | Found: E-400, E-401, E-420 | Elevation detail sheets should be included.
Elevation Details | Equipment Clearances | Pass | Pass | medium | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (FRONT VIEW) and (BACK VIEW), equipment arrangement area around AUX XFMR #1, MPZ, DAS MAIN ENCLOSURE ¦ The elevation shows equipment arrangement, but does not clearly state front, side, and back clearance dimensions for inverters/equipment. ¦ Value: Clearance references appear as typical equipment layout/elevations, but front/side/back code clearances are not explicitly tabulated | [AI] Elevation Details Review: Equipment Clearances
Elevation Details | Nec Clearance Table | Fail | Fail | medium | 32 | 0.72 | Location: Sheet E-400, all visible notes and title block areas ¦ No NEC clearance reference or compliance table is visible on this sheet. | [AI] Elevation Details Review: Nec Clearance Table
Elevation Details | Pile Depth | Pass | Pass | low | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (BACK VIEW), Notes section, Note 1 ¦ A note specifies a minimum 5' embedment depth below the concrete pad bottom. ¦ Value: Embedment depth of W6x9 piles must be at least 5' below bottom level of concrete pad | [AI] Elevation Details Review: Pile Depth
Elevation Details | Pile Spacing | Pass | Pass | low | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (FRONT VIEW), horizontal dimension line over rack bays labeled 4.5' ¦ The elevation shows a 4.5' dimension between support points across the rack. ¦ Value: 4.5' typical spacing shown between rack support piles; additional 8'-0" and 3'-5" vertical dims shown at rack section | [AI] Elevation Details Review: Pile Spacing
Elevation Details | Pile Type | Pass | Pass | low | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (BACK VIEW), note callout near rack support labeled 'W6X9 PILE (TYP.)' ¦ Pile type is explicitly called out as W6x9 pile typical. ¦ Value: W6x9 pile (typ.) | [AI] Elevation Details Review: Pile Type
Elevation Details | Sweep/Bend Distance | Pass | Pass | medium | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (FRONT VIEW) and (BACK VIEW), conduit routing beneath weather station, UPS, motor controller, and DAS main enclosure ¦ Conduit routing and sweep shapes are shown graphically, but no explicit bend distance or radius dimension is called out. ¦ Value: Conduit sweeps/bends are depicted; no specific bend radius or sweep distance is noted | [AI] Elevation Details Review: Sweep/Bend Distance
Elevation Details | Weather Sensors | Pass | Pass | low | 32 | 0.72 | Location: TYP. AUX RACK ELEVATION (FRONT VIEW) and (BACK VIEW), sensor callouts near top of rack ¦ Weather sensor mounting locations are clearly indicated with callouts for all-in-one sensor & GHI and GPS. ¦ Value: All-in-one sensor & GHI and GPS locations are shown at rack ends and near the top of the rack | [AI] Elevation Details Review: Weather Sensors
Engineered Equipment List | Equipment list sheet exists | Pass | Pass | medium | 4 | 0.96 | Found: E-050 | Engineered equipment list should be included.
Equipment Area Feeder Plan | Check NEC Table for clearance | Overridden / Accepted by QC Engineer | Needs Review | medium |  | 0.4 | Missing voltage for clearance lookup (Ref: NEC 110.26, Table 110.26(A)(1)) | Verify clearance values against NEC tables for working space around equipment. | Accepted by QC
Equipment Area Feeder Plan | Aux Power | Fail | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, feeder/grounding routes around AC Switchboard #1/#2 ¦ Aux power routing is not clearly shown on this sheet; only grounding and feeder/EGC paths are indicated. | [AI] Equipment Area Feeder Plan Review: Aux Power
Equipment Area Feeder Plan | Aux Rack | Fail | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, equipment layout near AC Switchboard #1/#2 and MV XFMRs ¦ No distinct AUX rack or cabinet is clearly identified on this sheet; the equipment shown appears to be inverters, switchboards, and transformers only. | [AI] Equipment Area Feeder Plan Review: Aux Rack
Equipment Area Feeder Plan | Equipment Clearances | Fail | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, inverter racks and transformer/switchboard equipment ¦ Manufacturer-required equipment clearances are not dimensioned or called out on this sheet. | [AI] Equipment Area Feeder Plan Review: Equipment Clearances
Equipment Area Feeder Plan | Equipment Faded | Pass | Pass | low | 41 | 0.72 | Location: Equipment Area Feeder Plan, general equipment layout (inverters, SWBDs, XFMRs) ¦ Equipment footprints and enclosures are shown in light gray while grounding/wiring is darker, allowing the wiring to remain legible. | [AI] Equipment Area Feeder Plan Review: Equipment Faded
Equipment Area Feeder Plan | Inverter Clearances | Fail | Fail | high | 41 | 0.72 | Location: Equipment Area Feeder Plan, inverter rack groups labeled INV 1, INV 13, INV 25, and INV 37 ¦ No minimum side, front, or rear clearance dimensions are shown for the inverter racks. | [AI] Equipment Area Feeder Plan Review: Inverter Clearances
Equipment Area Feeder Plan | Nec Clearances | Fail | Fail | high | 41 | 0.72 | Location: Equipment Area Feeder Plan, around AC Switchboard #1/#2 and MV XFMR #1/#2 ¦ Working clearances per NEC 110.26 are not dimensioned on the plan; clearance notes appear absent around the equipment pad area. | [AI] Equipment Area Feeder Plan Review: Nec Clearances
Equipment Area Feeder Plan | Nec Table Reference | Overridden / Accepted by QC Engineer | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, general notes/title block area ¦ There is no visible reference to NEC clearance tables on this sheet. | [AI] Equipment Area Feeder Plan Review: Nec Table Reference | Accepted by QC
Equipment Area Feeder Plan | Pad Type | Overridden / Accepted by QC Engineer | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, concrete pad callouts for Pad #1 and Pad #2 ¦ The plan labels concrete pads #1 and #2, but does not indicate whether the pad is individual or combined, and no gravel/material specification is shown. | [AI] Equipment Area Feeder Plan Review: Pad Type | Accepted by QC
Equipment Area Feeder Plan | Pile Details | Fail | Fail | medium | 41 | 0.72 | Location: Equipment Area Feeder Plan, inverter racks and equipment support areas ¦ Pile count, spacing, type, and embedment depth are not detailed for the inverter or auxiliary rack supports on this sheet. | [AI] Equipment Area Feeder Plan Review: Pile Details
Equipment Area Feeder Plan | Wiring Types | Pass | Pass | low | 41 | 0.72 | Location: Equipment Area Feeder Plan, conductor callouts around INV 1/13/25/37 and MV XFMR #1/#2 ¦ AC, DC, MV, and grounding/communication-type conductors are depicted with labeled routes such as inverter AC, inverter DC EGC, MV cables EGC, and grounding jumpers. | [AI] Equipment Area Feeder Plan Review: Wiring Types
Feeder Plan | Cab Fill Reference | Fail | Fail | medium | 18 | 0.72 | Location: Legend / System Information / Plan Notes ¦ A worst-case CAB fill reference is not visibly identified on this sheet. | [AI] Feeder Plan Review: Cab Fill Reference
Feeder Plan | Circuit Arrows | Pass | Pass | low | 18 | 0.72 | Location: Main Plan View, Feeder Runs ¦ Circuit direction/count indicators are shown along the feeder runs and at the connection points. | [AI] Feeder Plan Review: Circuit Arrows
Feeder Plan | Dcb/Inverter Labels | Pass | Pass | low | 18 | 0.72 | Location: Main Plan View / System Information Box ¦ DCB and inverter identifiers are shown on the plan and in the system information block, with inverter quantity listed and equipment labels placed near the feeder connections. | [AI] Feeder Plan Review: Dcb/Inverter Labels
Feeder Plan | Equipment Pads | Pass | Pass | low | 18 | 0.72 | Location: Main Plan View, Right Side Equipment Areas ¦ Equipment pad locations are depicted at the connection areas on the right side of the array blocks. | [AI] Feeder Plan Review: Equipment Pads
Feeder Plan | Feeder plan sheets exist | Pass | Pass | medium | 18 | 0.96 | Found: E-210, E-211, E-212, E-213, E-214, E-215, E-216, E-217 | Overall or equipment area feeder plan sheets should be present.
Feeder Plan | Fence And Road | Pass | Pass | low | 18 | 0.72 | Location: Plan Perimeter / Right Side Access Road ¦ Fence line is shown in the legend and on the plan perimeter, and the access road is shown along the right side of the layout. | [AI] Feeder Plan Review: Fence And Road
Feeder Plan | Legend | Pass | Pass | low | 18 | 0.72 | Location: Legend Box ¦ Legend is present and includes the cable types used on the plan, including UG MV cable, AC LV power line, AC LV tracker power line, DC feeder/harness output, and DC CB output line. | [AI] Feeder Plan Review: Legend
Feeder Plan | Scale And North Arrow | Pass | Pass | low | 18 | 0.72 | Location: Title Block / Bottom Center Scale Bar ¦ North arrow is shown in the right title block area, and a scale bar with "SCALE: 1" = 60'" is shown at the bottom center of the sheet. | [AI] Feeder Plan Review: Scale And North Arrow
Feeder Plan | Tracker Motor Cables | Pass | Pass | low | 18 | 0.72 | Location: Legend Box ¦ Tracker motor-related cabling is shown in the legend as AC LV tracker power line, indicating tracker motor cables are included where applicable. | [AI] Feeder Plan Review: Tracker Motor Cables
Feeder Plan | Trench Reference | Fail | Fail | medium | 18 | 0.72 | Location: Plan Notes / Title Block / Legend ¦ No explicit trench detail sheet reference or trenching detail callout is visible on this sheet. | [AI] Feeder Plan Review: Trench Reference
General Notes | General notes sheet exists | Pass | Pass | medium | 2 | 0.96 | Found: E-002 | A general notes sheet should be present.
Grounding Diagram | Bonding jumper and GEC sized | Overridden / Accepted by QC Engineer | Needs Review | medium |  | 0.4 | Missing transformer_kva or voltage for GEC calc (Ref: NEC 250.66) | Main bonding jumper shown and sized. GEC shown and sized per NEC 250.66. | Accepted by QC
Labels | Labels sheet exists | Pass | Pass | medium | 43 | 0.96 | Found: E-800 | Labels sheet should be included.
Overall Site Grounding Plan | Grounding sheets exist | Pass | Pass | medium | 9 | 0.96 | Found: E-130, E-500, E-501, E-502 | Grounding plan sheets should be present.
PAD / Slab Details | Pad or slab detail sheet exists | Pass | Pass | medium | 25 | 0.96 | Found: E-217, E-501 | Equipment pad or slab detail should be included.
PAD / Slab Details | Anchor Bolts | Fail | Fail | high | 41 | 0.72 | Location: Plan view, inverter rack / switchboard pad areas ¦ No anchor bolt layout, bolt sizes, or hold-down pattern is indicated on this sheet. ¦ Value: No anchor bolt pattern or sizes shown | [AI] PAD/Slab Details Review: Anchor Bolts
PAD / Slab Details | Concrete Specs | Fail | Fail | high | 41 | 0.72 | Location: Sheet E-501, plan notes and title block ¦ No concrete PSI or mix specification is shown in the visible plan notes. ¦ Value: No concrete strength specified | [AI] PAD/Slab Details Review: Concrete Specs
PAD / Slab Details | Drainage | Fail | Fail | medium | 41 | 0.72 | Location: Sheet E-501, plan view ¦ There are no visible grading slopes, drainage arrows, or pad drainage details around the equipment pads. ¦ Value: No drainage or grading notes shown | [AI] PAD/Slab Details Review: Drainage
PAD / Slab Details | Edge Details | Fail | Fail | medium | 41 | 0.72 | Location: Plan view, Concrete Pad #1 / Concrete Pad #2 areas ¦ The sheet shows pad outlines and grounding notes only; there are no sectioned edge or form details for the pad. ¦ Value: No edge/form detail shown | [AI] PAD/Slab Details Review: Edge Details
PAD / Slab Details | Grounding Connection | Pass | Pass | low | 41 | 0.72 | Location: Plan view, grounding notes near Concrete Pad #1 and #2 ¦ Grounding connections to the pad are shown, including grounding ring, ground rod, ground lug, and bonding jumpers. ¦ Value: Yes | [AI] PAD/Slab Details Review: Grounding Connection
PAD / Slab Details | Pad Dimensions | Fail | Fail | high | 41 | 0.72 | Location: Plan view, Concrete Pad #1 / Concrete Pad #2 callouts ¦ Concrete pad callouts are shown for Concrete Pad #1 and #2, but no length, width, or thickness dimensions are legible on this sheet. ¦ Value: Pad dimensions not clearly shown | [AI] PAD/Slab Details Review: Pad Dimensions
PAD / Slab Details | Rebar Schedule | Fail | Fail | high | 41 | 0.72 | Location: Sheet E-501, title block / plan view ¦ This sheet is an equipment pad area grounding plan and does not show a rebar schedule, bar sizes, or spacing. ¦ Value: No rebar schedule visible on this sheet | [AI] PAD/Slab Details Review: Rebar Schedule
PVSyst Analysis Summary | PVSyst summary available | Overridden / Accepted by QC Engineer | Needs Review | low |  | 1 | No external PVSyst report was provided in this run. | PVSyst report is external. Upload support can be added later. | Accepted by QC
System Information Table | Azimuth | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'AXIS AZIMUTH', column 'value'. ¦ Value: 180° | [AI] System Info + Datasheets (2 pages): Azimuth
System Information Table | Dc/Ac Ratio | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'DC/AC RATIO', column 'value'. ¦ Value: 1.29 | [AI] System Info + Datasheets (2 pages): Dc/Ac Ratio
System Information Table | Derated Kva/Kw Rating | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'TOTAL AC SIZE'. This is the plant derated AC size, not a single inverter rating. ¦ Value: 6,000.000 kWac | [AI] System Info + Datasheets (2 pages): Derated Kva/Kw Rating
System Information Table | Gcr (Ground Coverage Ratio) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'GROUND COVERAGE RATIO', column 'value'. ¦ Value: 0.41 | [AI] System Info + Datasheets (2 pages): Gcr (Ground Coverage Ratio)
System Information Table | Interrow Spacing | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'INTER ROW SPACING', column 'value'. ¦ Value: 9.4' | [AI] System Info + Datasheets (2 pages): Interrow Spacing
System Information Table | Inverter Kva Rating | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table row 'INVERTER' and inverter datasheet technical data table ('Max. power' / type variants). ¦ Value: 110 kVA / 125 kVA | [AI] System Info + Datasheets (2 pages): Inverter Kva Rating
System Information Table | Inverter Kw Rating | Pass | Pass | medium | 1 | 0.72 | Found in: Inverter datasheet technical data table; nameplate/datasheet indicates 110 TL3-US and 125 TL3-US classes with 110 kW and 125 kW max active power. ¦ Value: 110 kW / 125 kW | [AI] System Info + Datasheets (2 pages): Inverter Kw Rating
System Information Table | Inverter Make And Model | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'INVERTER', column 'value'; also shown on inverter datasheet title. ¦ Value: KACO blueplanet 110 + 125 TL3-US | [AI] System Info + Datasheets (2 pages): Inverter Make And Model
System Information Table | Inverter Max Vdc, Mppt Voltage Range | Pass | Pass | medium | 1 | 0.72 | Found in: Inverter datasheet technical data table, rows for 'Max. recommended PV generator power' / 'MPP range' / 'Max. input voltage'. The page shows max input voltage as 1,100 V and MPP range around 200-1,000 V. ¦ Value: Max Vdc 1,100 V; MPPT range 200-1,000 V | [AI] System Info + Datasheets (2 pages): Inverter Max Vdc, Mppt Voltage Range
System Information Table | Inverter Quantity | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'INVERTER QUANTITY', column 'value'. ¦ Value: 48 | [AI] System Info + Datasheets (2 pages): Inverter Quantity
System Information Table | Module Stc Rating (Watts) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'STC', column 'value'; appears consistent with the First Solar Series 6 Plus datasheet on this page. ¦ Value: 465 W | [AI] System Info + Datasheets (2 pages): Module Stc Rating (Watts)
System Information Table | Module Temperature Coefficients | Pass | Pass | medium | 1 | 0.72 | Found in: First Solar Series 6 Plus datasheet, Temperature Coefficients table. These are shown in the electrical specifications section. ¦ Value: Pmax -0.23%/°C, Voc -0.24%/°C, Isc +0.04%/°C | [AI] System Info + Datasheets (2 pages): Module Temperature Coefficients
System Information Table | Module Voc, Vmp, Isc, Imp | Pass | Pass | medium | 1 | 0.72 | Found in: First Solar Series 6 Plus datasheet, Electrical Specifications table (standard test conditions). Values appear readable and internally consistent. ¦ Value: Voc 82.1 V, Vmp 68.5 V, Isc 7.01 A, Imp 6.79 A | [AI] System Info + Datasheets (2 pages): Module Voc, Vmp, Isc, Imp
System Information Table | Pitch | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'PITCH', column 'value'. ¦ Value: 16' | [AI] System Info + Datasheets (2 pages): Pitch
System Information Table | Pv Module Make And Model | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'MODULE', column 'value'; also supported by module datasheet title on this page. ¦ Value: First Solar FS-6465A-B-P | [AI] System Info + Datasheets (2 pages): Pv Module Make And Model
System Information Table | Racking Make, Model And Size | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'RACKING', column 'value'. ¦ Value: Nextracker NX Horizon; (121) 1P6x9, (60) 1X84, (1) 1X148, (1) 1X48 | [AI] System Info + Datasheets (2 pages): Racking Make, Model And Size
System Information Table | String Quantity (Total Strings) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'STRING QUANTITY', column 'value'. ¦ Value: 2,784 | [AI] System Info + Datasheets (2 pages): String Quantity (Total Strings)
System Information Table | String Size (Modules Per String) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'MODULES/STRING', column 'value'. ¦ Value: 6 | [AI] System Info + Datasheets (2 pages): String Size (Modules Per String)
System Information Table | Tilt Angle Or Tracker Rotation Angle | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'TILT', column 'value'. ¦ Value: ±52° | [AI] System Info + Datasheets (2 pages): Tilt Angle Or Tracker Rotation Angle
System Information Table | Total Ac Size (Kva Or Mva) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'TOTAL AC SIZE', column 'value'; title sheet also states 6,000,000 W AC. ¦ Value: 6,000.000 kWac / 6.0 MWac | [AI] System Info + Datasheets (2 pages): Total Ac Size (Kva Or Mva)
System Information Table | Total Dc Size (Kwp Or Mwp) | Pass | Pass | medium | 1 | 0.72 | Found in: System Information table, row 'TOTAL DC SIZE STC', column 'value'; also shown in title as 7,767,360 DC W. ¦ Value: 7,767.360 kWDC | [AI] System Info + Datasheets (2 pages): Total Dc Size (Kwp Or Mwp)
Title Block | Each page has a sheet number | Pass | Pass | medium |  | 0.96 | Found sheet numbers on all 44 pages. | Every sheet should show a valid sheet number in the title block.
Title Block | Each page has a sheet title | Pass | Pass | medium |  | 0.89 | Sheet titles were parsed on every page. | Every sheet should show a readable sheet title in the title block.
Title Block | Date | Pass | Pass | medium | 1 | 0.72 | Location: Revisions table, Date column; bottom sheet footer text ¦ Date is shown in the revisions table and footer text. ¦ Value: Revision table shows dates; bottom edge also has a small print date that appears to read 4/3/2023 11:34:10 AM | [AI] Title Block (p.1): Date
Title Block | Designer Name | Pass | Pass | medium | 1 | 0.72 | Location: Project Information block, Designed By row ¦ Designed By shows Dan Grainger. ¦ Value: Dan Grainger | [AI] Title Block (p.1): Designer Name
Title Block | Engineer Name | Pass | Pass | medium | 1 | 0.72 | Location: Project Information block, EOR row ¦ EOR/engineer name is shown as Ermocrates Castillo. ¦ Value: Ermocrates Castillo | [AI] Title Block (p.1): Engineer Name
Title Block | Epc Logo | Pass | Pass | medium | 1 | 0.72 | Location: EPC block, logo area ¦ An EPC company logo is present in the title block. ¦ Value: Priority Power | [AI] Title Block (p.1): Epc Logo
Title Block | Project Name | Pass | Pass | medium | 1 | 0.72 | Location: Project Name panel, vertical text; top-center title ¦ Project name is shown as WINFIELD. ¦ Value: WINFIELD | [AI] Title Block (p.1): Project Name
Title Block | Revision Number | Pass | Pass | medium | 1 | 0.72 | Location: Revisions table, Rev column ¦ Revision number is shown in the revisions table. ¦ Value: Rev 4 (appears in the revisions table) | [AI] Title Block (p.1): Revision Number
Title Block | Sheet Number | Pass | Pass | medium | 1 | 0.72 | Location: Sheet Number box, bottom-right corner ¦ Sheet number is shown as E-001. ¦ Value: E-001 | [AI] Title Block (p.1): Sheet Number
Title Block | Sov | Fail | Fail | medium | 1 | 0.72 | Location: Title Block, bottom-right panel (project information/title data area) ¦ No SOV field is shown in the title block. | [AI] Title Block (p.1): Sov
Title Block | Date | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, bottom-right corner, footer date stamp ¦ Date/time is shown in the title block footer as 4/25/2023 11:13:52 AM. ¦ Value: 4/25/2023 11:13:52 AM | [AI] Title Block (p.22): Date
Title Block | Designer Name | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, right side, company identification block ¦ Designer name is shown as Castillo Engineering Services, LLC. ¦ Value: Castillo Engineering Services, LLC | [AI] Title Block (p.22): Designer Name
Title Block | Engineer Name | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, right side, company identification block ¦ Engineer name is shown in the company identification block as Castillo Engineering Services, LLC. ¦ Value: Castillo Engineering Services, LLC | [AI] Title Block (p.22): Engineer Name
Title Block | Epc Logo | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, right side, company logo blocks ¦ Company logos are present in the title block, including Castillo Engineering, KPP Energy, and Priority Power. ¦ Value: Castillo Engineering / KPP Energy / Priority Power logos | [AI] Title Block (p.22): Epc Logo
Title Block | Project Name | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, right side, PROJECT NAME block ¦ Project name is shown as WINFIELD. ¦ Value: WINFIELD (37.186064, -97.028902) | [AI] Title Block (p.22): Project Name
Title Block | Revision Number | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, right side, REVISIONS table ¦ Revision number is shown in the revisions table as Rev 2. ¦ Value: Rev 2 | [AI] Title Block (p.22): Revision Number
Title Block | Sheet Number | Pass | Pass | medium | 22 | 0.72 | Location: Title Block, bottom-right, SHEET NUMBER field ¦ Sheet number is shown as E-214. ¦ Value: E-214 | [AI] Title Block (p.22): Sheet Number
Title Block | Sov | Fail | Fail | medium | 22 | 0.72 | Location: Title Block, bottom-right corner, SOV field ¦ No SOV label or field is shown in the title block. | [AI] Title Block (p.22): Sov
Title Block | Date Shown | Pass | Pass | medium | 44 | 0.72 | Location: Sheet footer/border text, bottom edge near center-right ¦ A date is visible in the footer text along the bottom edge of the sheet. ¦ Value: 04/06/2023 | [AI] Title Block (p.44): Date Shown
Title Block | Designer Name Shown | Fail | Fail | medium | 44 | 0.72 | Location: Title Block, designer/author field not shown ¦ The title block does not display a separate designer name field. | [AI] Title Block (p.44): Designer Name Shown
Title Block | Engineer Name Shown | Fail | Fail | medium | 44 | 0.72 | Location: Title Block, engineer field not shown ¦ The title block does not display a separate engineer name field. | [AI] Title Block (p.44): Engineer Name Shown
Title Block | Epc Logo Present | Pass | Pass | medium | 44 | 0.72 | Location: Title Block, EPC field ¦ The PriorityPower logo is shown in the EPC box of the title block. ¦ Value: PriorityPower logo | [AI] Title Block (p.44): Epc Logo Present
Title Block | Project Name Shown | Pass | Pass | medium | 44 | 0.72 | Location: Title Block, PROJECT NAME field ¦ The project name field shows WINFIELD with coordinates and address text. ¦ Value: WINFIELD (37.186064, -97.028902) 202ND RD, WINFIELD, KS, 67156 | [AI] Title Block (p.44): Project Name Shown
Title Block | Revision Number Shown | Pass | Pass | medium | 44 | 0.72 | Location: Title Block, REVISIONS table ¦ The title block includes a revisions table, indicating revision tracking is present. ¦ Value: REV table present | [AI] Title Block (p.44): Revision Number Shown
Title Block | Sheet Number Shown | Pass | Pass | medium | 44 | 0.72 | Location: Title Block, SHEET NUMBER field ¦ The sheet number box reads E-900. ¦ Value: E-900 | [AI] Title Block (p.44): Sheet Number Shown
Title Block | Sov Present | Fail | Fail | medium | 44 | 0.72 | Location: Title Block, bottom-right, no SOV row/field shown ¦ The title block shows owner, EPC, project ID, project name, sheet name, sheet size, and sheet number, but no SOV field. | [AI] Title Block (p.44): Sov Present
Trenching Details | Trenching detail sheet exists | Pass | Pass | medium | 38 | 0.96 | Found: E-450, E-451 | Conduit trenching detail sheet should be included.
Trenching Details | Ampacity Notes | Fail | Fail | medium | 39 | 0.72 | Location: E-451, Sheet notes and detail annotations ¦ No ampacity derating notes for burial depth or soil conditions are shown on this sheet. | [AI] Trenching Details Review: Ampacity Notes
Trenching Details | Comms Cable | Pass | Pass | low | 39 | 0.72 | Location: E-451, Detail 1 (Medium Voltage Conductors with Communication Cables Trench Details) ¦ Communication cables are explicitly shown in 2" PVC SCH40 conduit in the trench detail. | [AI] Trenching Details Review: Comms Cable
Trenching Details | Conduit Spacing | Pass | Pass | medium | 39 | 0.72 | Location: E-451, Detail 2 (MV Circuits Road Crossing Details), spacing callouts near conduits ¦ The sheet calls out cable/conduit separations such as 12" MIN (TYP), 9" MIN (TYP), and 6" TYP, but it does not clearly dimension every conduit spacing to a feeder-plan count on this sheet. | [AI] Trenching Details Review: Conduit Spacing
Trenching Details | Dimensions | Pass | Pass | medium | 39 | 0.72 | Location: E-451, Details 1-3, width callout under trench sections ¦ The details show depth and some spacing dimensions, but trench width is only shown as 'varies' and not fully dimensioned for all configurations. | [AI] Trenching Details Review: Dimensions
Trenching Details | Direct Buried Vs Conduit | Pass | Pass | low | 39 | 0.72 | Location: E-451, Details 1-3, cable/conduit callout leaders ¦ Cable types are clearly identified as MV AC in 5" PVC80 conduit, MV AC cables in 4" conduit, and communication cables in 2" PVC SCH40 conduit, with no ambiguous direct-buried condition shown here. | [AI] Trenching Details Review: Direct Buried Vs Conduit
Trenching Details | Gnd Wire | Fail | Fail | medium | 39 | 0.72 | Location: E-451, Details 1-3 ¦ No ground wire is explicitly labeled or depicted in the conduit/trench details on this sheet. | [AI] Trenching Details Review: Gnd Wire
Trenching Details | Sheet Reference | Pass | Pass | medium | 39 | 0.72 | Location: E-451, Detail callout bubbles and titles ¦ The detail bubbles reference sheet E-451, but there is no explicit feeder plan sheet reference back to a specific plan sheet shown here. | [AI] Trenching Details Review: Sheet Reference
Trenching Details | Trench Depth Vs Voltage | Pass | Pass | low | 39 | 0.72 | Location: E-451, Details 1-3 (Medium Voltage Conductors with Communication Cables Trench Details; MV Circuits Road Crossing Details; MV Line Road Crossing Trench Details) ¦ Medium Voltage trench details show 36" MIN at the road crossing and 18" MIN for the MV/communications trench detail, which is consistent with MV depth requirements shown on the sheet. | [AI] Trenching Details Review: Trench Depth Vs Voltage
Trenching Details | Trench Headers | Pass | Pass | medium | 39 | 0.72 | Location: E-451, Detail titles and right-side sheet title block ¦ The trench detail headers are descriptive, but no feeder plan sheet references or specific circuit identifiers are shown on this detail sheet to verify matching plan references. | [AI] Trenching Details Review: Trench Headers
Trenching Details | Worst Case | Pass | Pass | medium | 39 | 0.72 | Location: E-451, Details 1-3 ¦ The sheet appears to show representative trench conditions, including a road crossing and a sloped side-view crossing, but it is not explicitly labeled as the worst-case trench configuration. | [AI] Trenching Details Review: Worst Case